## point 3 discharge
Licence point 3 - Final treated effluent quality monitoring before discharge to waterways (Burrangong Creek via flume)
EPA licence number: 1624 | [8 empty] | Sampling frequency: Monthly
Young Sewerage Scheme | [8 empty] | Sampling method: Grab sample
Reporting year: 2025-2026 | [8 empty] | Requirement to monitor concentration of pollutants discharged as per Licence Condition M2.1
|  |  | Pollutant | pH | Total Suspended Solid (TSS) | Oil and Grease (O&G) | Biological Oxygen Demand (BOD) | Ammonia as Nitrogen (NH3-N) | Total Nitrogen (TN) | Total Phosporus (TP) | Faecal Coliforms (FC) | Salinity
|  |  | Units of measure | - | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | CFU/100mL | uS/cm
|  |  | 100 % Licence Limit | 6.5-8.5 | 20 | 10 | 15 | 5 | 15 | 1 | 600 | NA
|  |  | 90% Licence Limit |  | 15 | 2 | 10 | 2 | 10 | 0.5 | 200
Sample date | Date results obtained | Date results published | [10 empty] | Comments
2025-07-09 | 2025-07-18 | 2025-08-05 |  | 7.47 | 2 | <1 | <2 | 0.3 | 2.57 | 0.26 | 2
2025-08-13 | 2025-08-14 | 2025-09-02 |  | 7.09 | <2 | <1 | <2 | 0.6 | 2.33 | 0.63 | <2
2025-09-16 | 2025-09-17 | 2025-10-01 |  | 7.53 | <2 | <1 | <2 | 0.4 | 2.4 | 0.12 | <2
2025-10-21 | 2025-10-29 | 2025-11-04 |  | 7.77 | <2 | <1 | <2 | 0.2 | 2.31 | 0.29 | 30
2025-11-28 | 2025-12-08 | 2025-12-09 |  | 7.7 | <2 | <1 | <2 | 0.1 | 1.85 | 0.39 | 6
2025-12-09 | 2025-12-10 | 2026-01-15 |  | 6.76 | <2 | <1 | <2 | <0.1 | 2.11 | 0.32 | 42
2026-01-06 | 2026-01-14 | 2026-02-02 |  | 7.67 | 3 | <1 | <2 | 0.3 | 1.77 | 0.24 | 140
2026-02-27 | 2026-03-10 | 2026-03-10 |  | 7.64 | 3 | <1 | <2 | 0.6 | 2.54 | 0.51 | 860
|  |  | Min | 6.76 | 2 | 0 | 0 | 0.1 | 1.77 | 0.12 | 2
|  |  | Max | 7.77 | 3 | 0 | 0 | 0.6 | 2.57 | 0.63 | 860
|  |  | Mean | 7.4538 | 2.6667 | #DIV/0! | #DIV/0! | 0.35714 | 2.235 | 0.345 | 180
`