## Sheet1
Licence point 2 - Final treated effluent quality monitoring in POND 4 before discharge to waters (Murrimboola Creek)
EPA licence number: 2866 |  |  |  | Sampling frequency: Any pollutant are sample monthly during discharge except for "Chlorophyll a" which is required to be monitored monthly
Harden Sewerage Scheme |  |  |  | Sampling method: Grab sample
ALS Sample Point: HARD20 |  |  |  | Requirement to monitor concentration of pollutants discharged as per Licence Condition M2.1
Reporting year: 2026-2027
|  |  | Pollutant | pH | Electrical Conductivity @ 25°C | Total Dissolved Solids (TDS) | Total Suspended Solids (TSS) | Oil and Grease | Biochemical Oxygen Demand (BOD) | Ammonia as N | Nitrite + Nitrate as N | Total Nitrogen as N | Total Phosphorus as P | Thermotolerant Faecal Coliforms (Confirmed) | Thermotolerant Faecal Coliforms (Presumptive) | Chlorophyll a
|  |  | Units of measure | pH Unit | µS/cm | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | CFU/100mL | CFU/100mL | µg/L
|  |  | Licence Limit | 6.5-8.5 | n/a | n/a | 30 | n/a | 20 | n/a | n/a | n/a | n/a | n/a | n/a | 100 (Exemption limit)
Sample date | Issue Date | Date results published | [14 empty] | Comments
2026-07-01 | 2026-07-08 | 2026-08-12 |  | 7.52 | 815 | 438 | 4 | <1 | <2 | 7.4 | 16 | 23.8 | 7.37 | 90 | 90 | 2.99
2026-08-04 | 2026-08-10 | 2026-08-12 |  | 7.47 | 820 | 312 | 6 | <1 | 3 | 6.2 | 16.5 | 25.4 | 6.88 | 14 | 14 | 4.7
2026-09-07 | 2026-09-15 | 2026-09-16 |  | 7.59 | 715 | 365 | 16 | <1 | 3 | 5.6 | 17.3 | 23.2 | 6.69 | 38 | 38 | 2.83
|  |  | Min | 7.47 | 715 | 312 | 4 | 0 | 3 | 5.6 | 16 | 23.2 | 6.69 | 14 | 14 | 2.83
|  |  | Max | 7.59 | 820 | 438 | 16 | 0 | 3 | 7.4 | 17.3 | 25.4 | 7.37 | 90 | 90 | 4.7
|  |  | Mean | 7.5267 | 783.3333 | 371.6667 | 8.6667 | #DIV/0! | 3 | 6.4 | 16.6 | 24.1333 | 6.98 | 47.3333 | 47.3333 | 3.5067
As per Licence 2866 Limit Conditions
Note: | L2.5 The licensee is not taken to have exceeded a quality limit specified in this licence for Biochemical Oxygen Demand, pH or Total Suspended solids if:
(a) monitoring by the licensee shows that the level of chlorophyll a in the maturation ponds during any exceedence was 100ug/L or more (showing that the exceedence was caused by excessive algal growth); and
(b) the liquid waste entering the maturation ponds during the exceedence complies with the quality limit.
`